# Inspecting Motor Bearings

#### For predictive maintenance, thermography is a good alternative to vibration analysis for bearings that are relatively small, in low-speed operations, or when bearings are physically inaccessible or unsafe to get close to while the equipment is running.

By Colin Plastow, MRO Magazine, September 2010

Thermography is used in many predictive maintenance (PdM) programs today to monitor the temperatures of operational equipment. With thermal imagers, technicians can capture two-dimensional infrared maps (images) of bearing and housing temperatures, which enables them to compare current operating temperatures against benchmarks and detect potential failures and avoid equipment loss. This article will examine typical thermography applications for inspecting bearings.

Consider this scenario: A motor bearing fails, the motor heats up and lubrication begins to break down. The windings overheat and then the temperature sensor cuts out and stops the motor. In the worst case, the shaft binds up, the rotor locks up and the motor fails completely.

What to check: Generally speaking, vibration analysis is the PdM technology of choice for monitoring large, accessible, relatively high-speed bearings, but it can only be done safely when transducers can be placed on the bearings. Thermography is a good alternative to vibration analysis for bearings that are relatively small (e. g., in conveyor rollers), in low-speed operations, or when bearings are physically inaccessible or unsafe to get close to while the equipment is running.

In most cases, thermography can be performed at a safe distance while the equipment is operating. Capturing a thermal image with a handheld imager also takes less time than performing vibration analysis.

Mechanical equipment should be inspected when it has warmed up to a steady-state condition and is running a normal load. That way, measurements can be interpreted at normal operating conditions.

The first step is to capture a thermal image of the bearing to be checked, and if possible, to capture images of bearings in the same area performing the same or a similar function, e.g., the bearing at the other end of a conveyor or paper machine roller, or another pillow block on the same shaft.

Identifying potential problems

Problems with bearings are usually found by comparing the surface temperatures of similar bearings working under similar conditions. Overheating conditions appear as hot spots within an infrared image and are usually found by comparing similar equipment. In checking motor bearings, this procedure entails comparing end bell to end bell (for motors and bearings of the same type) or stator to end bell temperatures.

In general, it is a good idea to create a regular inspection route that includes all critical rotating equipment. If a route for regular vibration analysis already exists, thermography can be added easily to these existing bearing monitoring efforts.

Once the inspection has been completed, save a thermal image of each piece of key equipment that has been inspected on a computer and use the software that comes with the thermal imager to track these measurements over time. This will provide baseline images that will help you determine whether a hotspot is unusual or not and help you verify when repairs are successful.

What represents a red alert? Equipment conditions that pose a safety risk should take the highest repair priority. Beyond that, determining when action is required to keep a bearing from causing the loss of a crucial piece of equipment is a case-by-case undertaking that gets easier with experience.

For example, on one difficult-to-monitor line, an auto manufacturer moved from vibration analysis to a combination of vibration and thermography to determine that normal operating temperatures for bearings on the line fell within a specific range. The company's PdM personnel, well trained in thermography, now treat a bearing running above the upper limit of the normal operating range as an alarm situation.

When using thermography on bearings that are not normally monitored using vibration analysis, or even when spot-checking bearings, try to establish alarm criteria, as you would for other condition- monitoring technologies. Some thermography experts, for example, have established rules-of-thumb for allowable temperature differentials for bearings on specific types of equipment using specifi c lubrication techniques (grease, oil bath, etc.).

The potential cost of failure

For a failed bearing in a specific motor, pump, drive or some other critical component, analyzing the cost of the repair, lost production opportunity and lost labour costs will provide the total potential cost of the failure.

All rotating equipment generates heat at the friction- bearing points in the system -- the bearings. Lubrication reduces friction and thereby reduces and, to varying degrees (depending upon the type of lubrication), dissipates the heat. Thermal imaging allows you to capture this process with images -- while also revealing the condition of the bearings.

When thermal images indicate an overheating bearing, you should generate a maintenance order to either replace the bearing or lubricate it. Vibration analysis or another PdM technology may help determine the best course of action. Using the software associated with the thermal imager to document your findings, including a thermal image and a digital image of the equipment, is the best way to communicate the problems you find and to suggest repairs.

With motors accounting for the majority of the electricity consumed by industry, an integral part of optimizing performance and minimizing downtime is having the ability to capture information on a motor's temperature profile. Using thermal imaging to perform routine checks can play an important role in making sure that motors are running at peak efficiency at all times, while avoiding costly and time-consuming repairs.

Colin Plastow has been with Fluke Electronics Canada since 1987 in various support and product management positions. Today, as industrial product manager for Fluke, he brings his expertise in electronic test and measurement to customers in high-tech and industrial markets.